## Slide 1: Final presentation
Cost-effective Monitoring System for Biomedical and Cleanroom Facilities
EE499 – Winter 2022
Team 8

## Slide 2: General project information
Project Title
Cost-effective Monitoring System for Biomedical and Cleanroom Facilities
Project Timeline
December 2022 – November 2023
Project Sponsor
King Abdulaziz University, Faculty of Engineering, Department of Electrical and Computer Engineering

## Slide 3: Customer & Advisor
Abdullah Abu bakr Alkaf (ECE)
aalkaf0013@stu.kau.edu.sa
+966508393281
Team#08
Dr. Nebras Sobahi
nsobahi@kau.edu.sa
Ibrahim Mohammed Ahmed (ECE)
iibrahimahmed@stu.kau.edu.sa
+966500954858
Omar Abdulaziz Hussain (ECE)
Omoosaharoonamirhussain@stu.kau.edu.sa
+966507621903
#1
#2
#3
Project Stakeholders

## Slide 4: agenda
1. Introduction
2. Conceptual Design
4. Implementation Plan
5. Results and Evaluation
7. References
3. Product baseline Design
6. Conclusion

## Slide 5: 1. Introduction
About the project
Background information

## Slide 6: About the project
What is cleanroom?
Include critical processes
Sensitive from particle
Closed regulated environment
Examples of cleanroom
Surgery rooms
Material storage rooms
Laboratory rooms

## Slide 7: Background information
Cleanroom Classifications
The Federal Standard 209 ( FS 209E )
Ex: Class 100,000 – Class 1,000
ISO 14644-1 standard
Ex: ISO1, ISO2,…ISO9
Source: : Lourdes M. Caselli-Fernández1
, Dr. Robert, Clean room environment, personnel, quality assurance and
their monitoring, https://rb.gy/yeh44g

## Slide 8: Background information
Statement-Restatement Method
KT Decision Analysis

## Slide 9: 2. Conceptual design
Situation Description
Problem Definition
Project Objectives
Realistic Constraints
Product design specifications (PDS)
Literature Review
Analyzing Alternative Solutions
Maturing Baseline Design

## Slide 10: Situation Description
Fires & Disasters.
Gas leakage accidents.
Damaging materials & Equipment.
Expensive available products in the market.
[A]
[B]
Sources:
[A] (Disaster Strikes Supply Chain Again &#8211; Another Chip Factory Destroyed by Fire, 2021)
[B] (India Gas Leak: At Least 11 Dead After Visakhapatnam Incident, 2020)

## Slide 11: Problem definition
Initial problem statement
Monitoring systems for biomedical and cleanroom facilities are mostly expensive.
Final problem statement
the available monitoring systems are mostly expensive and not suitable for all kinds of cleanrooms.

## Slide 12: Project objectives
High-level Objectives
Cost effective monitoring system
Monitoring system for any regulated environment
Expandable monitoring system
Low-level Objectives
Monitoring the environment inside the cleanroom
Detecting particles in air
Alarming system

## Slide 13: Realistic constraints
The total cost of the product must not exceed 3,500 SR.
The operations inside the cleanroom must not be affected by the product’s material.
The product must always be in operation mode.
The product must be able to be completed by the scheduled deadline.

## Slide 14: Product design specifications
In-scope objectives (Musts)
Out-scope objectives (Wants)
Realistic assumptions

## Slide 15: in-scope objectives (must)
Expandable and capable to accommodate multiple
sub-systems
The system Monitor by it-self without human intervention
The system must have backup battery in case of blackout happen
The system should monitor the temperature, humidity, and particles in air inside the cleanroom.
The design send alarming SMS massages.

## Slide 16: out-scope objectives (wants)
the cost of the design doesn’t exceed 2,500 SR
The product can detect motions inside the cleanroom
The design is Affordable for any kind of cleanroom
The design can use Wi-Fi in the alarming system
The product displays the data continuously via internet website

## Slide 17: Realistic Assumptions
Provided power supply
Availability of product’s components in local market
Controlled air conditioning

## Slide 18: Literature review
Internet of Things (IoT) Monitoring System of a Modeled Cleanroom[1]
Internet of things (IoT) humidity and temperature monitoring system[2]
Previous Projects

## Slide 19: Cont. Previous projects
Gas and Air Quality Detection, and Monitoring Using Embedded System for Nanofabrication Facility[3]

## Slide 20: Cont. Literature review
Section-1
Basic components of cleanrooms
Section-2
Designing and construction of cleanrooms
Section-3
Operations and monitoring in cleanrooms
Section-4
Quality management in cleanrooms
Section-5
Clinical outcomes and new developments
Section-6
International experience and some case studies
Cleanroom Technology in ART Clinic: A Practical Guide[4]

## Slide 21: Available products in market
Clean room Monitoring system B13-200-OTA by Co. senso scientific[5]
USP 800 Hard wall Cleanrooms for Hazardous Drug Compounding by CO. Terra universal[6]
Price: 7,989 SR
Temp Measurement Range:
-40°F to 257°F (-40°C to 125°C)
Humidity Range: 0% to 100% RH
Tolerance: ±0.5°C; ±2% RH (0% RH to 90% RH and 0°C to 60°C)
RF Frequency: 2.4 to 2.497 GHz
ISO Class : ISO-7
Price: 98,864 SR
Application: USP 800 (Sterile HD)
Width: 12', 10', 16’
Depth: 12', 10', 6', 8’
Height: 8’
Panel Material: Polypropylene
ISO Class: ISO 5
Features available for logging and storing room pressures and temperature
Pressure sensor included in each room

## Slide 22: Cont. Available products in market
Product specifications:
Price: 27,651 SR
Differential Pressure Sensor (with NIST calibration certificates)
Temp/Humidity sensor (with NIST calibration certificates) DPS Differential Air Pressure Sensor: Accuracy: +/- 0.25%, Range: +/- 4 in H2O
Temp Range: -10˚C to +80˚C / Humidity Range: 0-80% RH
Clean Room Monitoring System – THP-303[8]
Product specifications:
Price: 1,856 SR
Temperature range: -40.0 to 60.0 °C /-40.0 to 140.0 °F
Temp accuracy: +/- 0.3 °C/ °F
RH% Range: 0.0 to 100.0 %RH
RH Accuracy: +/-1.0 %RH
Diff. Pressure Range: +/-100 mmWC or +/-999 Pascal
DP Accuracy:+/- 1% of the calibrated range.
Cleanroom Monitoring – 3 Room Kit By CO. SONICUE[7]

## Slide 23: Alternative designs

## Slide 24: ALTERNATIVE 1
- Components:
Relay (5V)
Battery(5V)
Humidity and Temperature sensors (SHT20)
Pressure sensors (BMP280)
ESP32 Wi-Fi module
Blynk Application
Twilio website

## Slide 25: ALTERNATIVE 2
- Components:
Relay (5V)
Battery (5V)
Humidity and Temperature sensors (SHT20)
Pressure sensors (BMP280)
GSMS900A
Raspberry Pi
Multiplexer (CD74HC4051-EP)

## Slide 26: ALTERNATIVE 3
- Components:
Relay (5V)
Battery (5V)
Humidity and Temperature sensors (SHT20)
Pressure sensors (BMP180)
Arduino Nano
ESP32 SIM800l

## Slide 27: Pros & cons
Alternative | Advantages | Disadvantages
1 | Display Screen For System’s status Low Cost Small Size | Internet dependent system Covers Short Area
2 | Covers Long Area Flexibility of Input’s Number Range | MUX Delay
3 | High Precision Failure Detection | High Cost More Components

## Slide 28: BASELINE DESIGN SELECTION

## Slide 29: Kt decision analysis
KT Decision Analysis |  |  |  | 
Artifacts: |  | Alternative 1 | Alternative 2 | Alternative 3
Must | The system has the capability to monitor the internal environment and connect to multiple sub-systems inside the cleanroom as much as needed. | GO | GO | GO
 | The system must monitor by itself without human intervention. | GO | GO | GO
 | Include backup rechargeable battery for power outages situations that last at least for three hours. | GO | GO | GO
 | The system must measure the humidity, pressure, and temperature. | GO | GO | GO
 | The system can alarm safety and security departments by sending SMS messages. | GO | GO | GO

## Slide 30
KT Decision Analysis |  |  |  |  |  |  | 
Artifacts: |  | Alternative 1 |  | Alternative 2 |  | Alternative 3 | 
Wants | Weight | Rate | Score | Rate | Score | Rate | Score
The cost is lower than 2,500 SR. | 8 | 8 | 64 | 7 | 56 | 2 | 16
The system detects motions in staff area to protect passed out people. | 7 | 4 | 28 | 8 | 56 | 5 | 35
The system can work with several kinds of cleanrooms (Semiconductor cleanroom, biomedical facilities, controlled storage). | 6 | 4 | 24 | 7 | 42 | 6 | 36
The system can use Wi-Fi in the alarming system | 5 | 7 | 35 | 3 | 15 | 6 | 30
Touch screen used to display the parameter adjustment | 4 | 7 | 28 | 4 | 16 | 3 | 12
 |  | Total 1 =179 |  | Total 2=185 |  | Total 2 =129 | 
Kt decision analysis

## Slide 31: Maturing baseline design
Added sensors:
RCLW-0516 Motion Sensor
Thing speak cloud
NH3 (MQ-137), Methane(MQ-4), Smoke (MQ -2) Gas Sensors
Approved microprocessor:
ESP32 SIM800l
Enhance processing performance
Reduces cost
Simplifies the design

## Slide 32: 3. Product baseline design
Matured baseline Block Diagram
Flow Chart
Ranges and Characteristics of Variables

## Slide 33: Matured baseline block diagram

## Slide 34: Flow Chart

## Slide 35: Ranges and Characteristics of Variables
Temperature degree [9]
20° - 24°( + 1 degree's variation)
Relative humidity [9]
30% - 60% ( + 5% degree's variation)
Atmospheric Pressure [10]
1013 hPa ( + 10 hPa Variation)
Particles [11]
Particles size > 0.1 um [ (100,000) particle/m3 ]
Particles size > 0.2 um [ (23,700) particle/m3]
Particles size > 0.3 um [ (10,200) particle/m3 ]
Particles size > 0.5 um [ (3,520) particle/m3 ]
Particles size > 1 um [ (832) particle/m3 ]
Particles size > 5 um [ (29) particle/m3 ]

## Slide 36: 4. Implementation plan
Validation of Essential Sub-systems
Final Comprehensive System

## Slide 37: Validation of essential sub-systems
Gases Monitoring Subsystem
Motion Monitoring Subsystem
Temperature & Humidity Monitoring Subsystems
Particle detecting Subsystem
Pressure Monitoring Subsystem
SMS Alarming System

## Slide 38: gases monitoring subsystem
Equipment
Breadboard
Connection wires
ESP32 SIM800l microcontroller
1K ohm Resistor
Mux CD774HC4051-EP
Gas sensor MQ-137
Gas sensor MQ-4
Gas sensor MQ-2

## Slide 39: motion monitoring subsystem
Equipment
Breadboard
Connection wires
ESP32 SIM800l microcontroller
1K ohm Resistor
Analog Mux CD774HC4051-EP
Motion sensor RCWL-0516

## Slide 40: temperature, AND humidity monitoring subsystems
Equipment
Breadboard
Connection wires
Arduino Uno
I2c Mux TCA9548A
Temperature and Humidity sensors (SHT20)

## Slide 41: PRESSURE monitoring subsystem
Equipment
Breadboard
Connection wires
Arduino Uno
I2c Mux TCA9548A
Pressure sensors (BMP280)

## Slide 42: particle detecting subsystem
Equipment
Breadboard
Connection wires
ESP32 SIM800l microcontroller
Particle sensor (PMS9003M)

## Slide 43: Validating SMs Alarming system
Equipment
Breadboard
Connection wires
ESP32 SIM800l microcontroller
1K ohm Resistor
Switch

## Slide 44: Final Comprehensive system

## Slide 45: Final product version 1

## Slide 46: Final product version 2

## Slide 47: Final product version 2

## Slide 48: 5. Results and evaluation
Results
Technical Aspects
Impacts of The Design
Financial Aspects
Applicable engineering standards

## Slide 49: Results of Gases Monitoring Subsystem
Threshold = 2.5 V

## Slide 50: Results of Particle detecting Subsystem
Threshold for P >0.5um
= 3,520
Threshold for P >0.3um=
10,200
Threshold for P >1um
= 832

## Slide 51: Results of Particle detecting Subsystem

## Slide 52: Results of Particle detecting Subsystem

## Slide 53: Results of Motion Monitoring Subsystem
Threshold = 2.5 V

## Slide 54: Results of Temperature & Humidity Monitoring Subsystem
Lower limit = 19 C°
Upper limit = 25 C°

## Slide 55: Results of Temperature & Humidity Monitoring Subsystem
Upper limit = 65%
Lower limit = 25%

## Slide 56: Results of Pressure Monitoring Subsystem
Upper limit = 1023 hPa
Lower limit = 1003 hPa

## Slide 57: Results of SMs Alarming system

## Slide 58: Results of The Final Comprehensive Prototype
Motion Sensor-1
Motion Sensor-2
Empty
Channels

## Slide 59: Results of The Final Comprehensive Prototype
Smoke Sensor
Methane Sensor

## Slide 60: Results of The Final Comprehensive Prototype
Pressure Sensor-1
PressureSensor-2
Empty
Channels

## Slide 61: Results of The Final Comprehensive Prototype
Temp Sensor-1
Empty
Channels
Empty
Channel

## Slide 62: Results of The Final Comprehensive Prototype
Empty
Channels
Empty
Channel
Hum Sensor-1

## Slide 63: Applicable engineering standards
ISO 14644-1 (Particle classification standard)[12]
Saudi Council of Engineers (SCE)[13]
GE-T9 (Magnetism and Electricity)
GE-T12 (Project Management)
GE-T13 (Ethics and Professionalism)
Institute of Electrical and Electronics Engineers (IEEE)[14]
P802.11 (Standard for Information technology)

## Slide 64: Technical aspects
Cost-effective system
Suitable for several kinds of cleanrooms
Backup power system
Informing the user about the situation of the cleanroom continuously
The system is generic and able to work with additional subsystem

## Slide 65: Financial Aspects
Project Cost Analysis
#Number | Component | Quantity | Price (SR)
1 | 220AC – 5DC CONVERTER | 1 | 29
2 | Power Bank | 1 | 99
3 | Relay (5V) | 1 | 25
4 | BMP280 | 2 | 27
5 | SHT20 | 2 | 133
6 | RCLW-0516 | 2 | 15
7 | PMS9003M | 1 | 442
8 | CD74HC4051-EP | 2 | 24
9 | TCA9548A | 2 | 32
10 | ESP32 SIM800l | 1 | 91
11 | MQ-4 | 1 | 24
12 | MQ-2 | 1 | 35
13 | MQ-137 | 1 | 63
14 | SIM Card | 1 | 80
Total (SR) |  |  | 1,350

## Slide 66: Impacts of the design
Environment
Toxic Substances & Battery waste.
Society
Opportunities for small cleanrooms.
Global
Firms can get a cost-effective system.
Safety
Chemical, Electrical, and Radiational risks.
Financial
Effective from the economical side.

## Slide 67: 6. conclusion
The Challenges
Analyzing all the collected data at the same time.
The speed of the response from the microprocessor.
Solution
Precise monitoring system, that monitor temperature, relative humidity, atmospheric pressure, motion, toxic gases, and particles inside the cleanroom that follows ISO-5 classification.
Impact
Offering reliable and cost-effective monitoring system for small cleanrooms.

## Slide 68: Future work recommendations
Adding UART Mux
Develop serial communication for long-distance
Monitoring differential and positive pressure
Improve dual core performance of the ESP32 SIM800l microcontroller

## Slide 69: Rules and Responsibilities
M1 – Omar Abdulaziz Hussain
Motion Monitoring Subsystem (Software & Hardware)
Gases Monitoring Subsystem (Software & Hardware)
M2 – Ibrahim Mohammed Ahmed
Temperature & Humidity Monitoring Subsystem (Software & Hardware)
Particle Detecting Subsystem (Software & Hardware)
M3 – Abdullah Abu-Bakr Alkaf
SMS Alarming Subsystem (Software & Hardware)
ThingSpeak cloud data representation
Final Comprehensive Prototype (Software & Hardware)
Pressure Monitoring Subsystem (Software & Hardware)
Reports Responsible
Power Point slides designer
Reports Assistance
Power Points Slides Assistance
PCB Designer
Schematics and Blocks Designer
Team Leader

## Slide 70: 7. References
[1] M. I. Rosli and M. R. Ahmad, “Internet of things monitoring system of a modeled cleanroom,” ELEKTRIKA. [Online]. Available: https://elektrika.utm.my/index.php/ELEKTRIKA_Journal/article/view/283. [Accessed: 23-Feb-2023].
[2] E. A.- styleshout.com, “Research on the Temperature & Humidity Monitoring System in the Key Areas of the Hospital Based on the Internet of Things,”IJSH. [Online]. Available: https://gvpress.com/journal/IJSH/. [Accessed: 23-Feb-2023].
[3] “Gas and air quality detection, and monitoring using embedded system for ...” [Online]. Available: https://www.researchgate.net/profile/Damian-Valles/publication/327209768_Gas_and_Air_Quality_Detection_and_Monitoring_Using_Embedded_System_for_Nanofabrication_Facility/links/5b802f30a6fdcc5f8b6474a1/Gas-and-Air-Quality-Detection-and-Monitoring-Using-Embedded-System-for-Nanofabrication-Facility.pdf. [Accessed: 23-Feb-2023].
[4] “Clean room technology in art clinics,” Google. [Online]. Available: https://books.google.com.sa/books?hl=ar&lr=&id=ZmsNDgAAQBAJ&oi=fnd&pg=PA19&dq=monitoring%2Bsystem%2Bfor%2Bcleanrooms%2Bbased%2Bon%2Biso%2Bstandards&ots=uUTULW3z6b&sig=uOT9nPdwUkfkHkkjowPk_7HpIXU&redir_esc=y#v=onepage&q=monitoring%20system%20for%20cleanrooms%20based%20on%20iso%20standards&f=false. [Accessed: 23-Feb-2023].
[5] Cleanroom Monitoring System. (n.d.). https://www.laboratory-equipment.com/cleanroom-monitoring-system-sensoscientific.html
[6] USP 800 Hardwall Cleanrooms for Hazardous Drug Compounding. (n.d.). https://www.terrauniversal.com/usp-800-hardwall-clean-room-for-hazardous-drug-compounding.html
[7] Clean Room Monitoring - 3-Room Package. (n.d.). Sonicu. https://shop.sonicu.com/products/clean-room-monitoring-3-room-kit
[8] Clean Room Monitoring System – THP-303 – Libratherm Instruments. (n.d.). https://www.libratherm.com/product/clean-room-monitoring-system-thp-303/
Technologies, B. T. (2019, November 5). Taking a Look at Ideal Cleanroom Temperature and Humidity Standards. Blue Thunder Technologies. https://bluethundertechnologies.com/taking-a-look-at-idea-cleanroom-temperature-and-humidity-standards/ . [Accessed: 10-Sep-2023].
[9] IBM Research - Zurich. (n.d.). Cleanroom technology. https://www.zurich.ibm.com/pdf/nanocenter/Factstheet_Cleanroom_EN_2.pdf [Accessed: 10-Sep-2023].
[10] IBM Research - Zurich. (n.d.). Cleanroom technology. https://www.zurich.ibm.com/pdf/nanocenter/Factstheet_Cleanroom_EN_2.pdf [Accessed: 10-Sep-2023].
[11] Connect 2 Cleanrooms. (n.d.). ISO 14644-1 Class 5 Cleanroom Classification Guidelines. https://shorturl.at/prTW4 [Accessed: 10-Sep-2023].
[12] 1.https://www.researchgate.net/profile/Robert-Terkola/publication/281232293_Clean_room_environment_personnel_quality_assurance_and_their_Monitoring/links/5720766008aeaced788adba3/Clean-room-environment-personnel-quality-assurance-and-their-Monitoring.pdf
[13] H. Scott Fogler, and Steven E. LeBlanc, Strategies for Creative Problem Solving, Prentice Hall Publisher, Printed in U.S.A., 1995.
[14] “IEEE SA - IEEE standard for Telecommunications and information exchange between systems - LAN/man specific requirements - part 11: Wireless Medium Access Control (MAC) and Physical Layer (PHY) specifications: High speed physical layer in the 5 GHz Band,” IEEE Standards Association. [Online]. Available: https://standards.ieee.org/standard/802_11a-1999.html. [Accessed: 23-Feb-2023].
“ISO 14644-1:2015,” ISO, 13-Aug-2021. [Online]. Available: https://www.iso.org/standard/53394.html. [Accessed: 23-Feb-2023].

## Slide 71: Thank you!
Feel free to ask Questions